Network Alarm Host User’s Manual

V 1.0.0

Table of Contents

1	Product Overview	1

1.1	Introduction	1

1.2	Features	1

1.3	Port	1

2	Device Installation and Wiring	3

2.1	Device Installation	3

2.1.1	Project Installation	3

2.1.2	Motherboard Module Installation	3

2.2	Wiring	6

2.2.1	Host Wiring	6

2.2.2	Sensor Wiring	7

2.2.3	Alarm Output Wiring	8

3	SDK Client	10

3.1	Login	10

3.2	Device Configuration	10

3.2.1	Network	10

3.2.2	Time	11

3.2.3	Alarm Output	11

3.2.4	Arm/Unarm	12

3.2.5	Bypass	13

3.2.6	On/Off Zone	14

3.2.7	File Upload and Download	16

3.2.8	Modify Password	16

3.2.9	Battery Search	17

3.2.10	Mobile Business	17

3.2.11	Get Alarm Channel Status	18

3.2.12	Get Active Zone(defence area) Status	20

3.3	Device Management	20

3.3.1	Device Capacity	20

3.3.2	Alarm Subscription	21

3.3.3	Alarm Bell Control	22

3.3.4	Reboot Device	22

3.3.5	Reset	22

3.3.6	Log Management	22

3.3.7	Delete Log	23

3.3.8	File Search	23

3.3.9	Version	24

3.3.10	User	24

3.3.11	Remote Upgrade	25

4	Alarm Programming Keyboard	1

4.1	Wiring	1

4.2	Function	1

4.2.1	Before Operation	1

4.2.2	About Keyboard Operation	2

4.3	Arm-Unarm	2

4.3.1	Arm	2

4.3.2	Unarm	2

4.3.3	ByPass	3

4.3.4	Cancel ByPass	3

4.4	Zone Settings	3

4.4.1	Intime	3

4.4.2	Fullday	3

4.4.3	Delay	3

4.5	Door Setting	4

4.5.1	Mode	4

4.5.2	Status Control	4

4.6	Other Settings	4

4.6.1	Reset	4

4.6.2	Reboot	4

4.6.3	Initialization	4

4.6.4	Password	5

4.6.5	System Time	5

4.6.6	Keysound	5

4.7	Communication Setting	5

4.7.1	Net	5

4.7.2	Tel	6

4.7.3	GSM	6

4.7.4	RS485 Address	6

4.7.5	2G	6

4.7.6	Wireless Code	6

4.8	Output Setting	7

4.8.1	Alarm Bell	7

4.8.2	Alarm	7

4.9	System Status	7

4.9.1	Zone	7

4.9.2	Door	7

4.9.3	Version	7

4.9.4	System Time	7

4.9.5	Communication	8

4.9.6	AF Status	8

4.9.7	Output	8

5	FAQ	9

Welcome

Thank you for purchasing our Network Alarm Host!

This user’s manual is designed to be a reference tool for the installation and operation of your system.

Here you can find information about features and functions, as well as a detailed menu.

Before installation and operation please read the following safeguards and warnings carefully!

Important Safeguards and Warnings

1．Electrical safety

All installation and operation here should conform to your local electrical safety codes.

We assume no liability or responsibility for all the fires or electrical shock caused by improper handling or installation.

2．Transportation security

Heavy stress, violent vibration or water splash are not allowed during transportation, storage and installation.

3．Installation

Keep the device upwards. Handle it with care.

Do not apply power to the device before completing installation.

Do not place objects on the device.

4．Qualified engineers needed

All the examination and repair work should be done by the qualified service engineers.

We are not liable for any problems caused by unauthorized modifications or attempted repair.

5．Environment

The device should be installed in a cool, dry place away from direct sunlight, inflammable, explosive substances and etc.

6.  Accessories

Be sure to use all the accessories recommended by manufacturer.

Before installation, please open the package and check all the components are included.

Contact your local retailer ASAP if something is broken in your package.

7. Lithium battery

Improper battery use may result in fire, explosion, or personal injury!

When replace the battery, please make sure you are using the same model!

# Product Overview

## Introduction

The Network Alarm Host is a multifunctional alarm device combining Ethernet, PSTN network, GPRS transmission approach, and support for keyboard programming and remote control.

The products are mainly used in intelligent building alarm systems, residential homes and perimeter alarm systems, building security systems, as well as factories, schools, warehousing and other large security systems. It allows management on access platform software, easy to integrate with other systems.

## Features

- 10/100M self-adaptive network port.

- IP net, GPRS net, RSTN net alarm upload.

- Alarm link output and event trigger output.

- 4-ch local alarm output. AH2008 series product also supports 8-ch local alarm input. AH2016 series product 16-ch local alarm input.

- 1-ch controller alarm bell output (12V DC).

- Abundant user rights.

- 24-hour zone, instant zone, delay zone.

- 5 groups of mobile phone setup with alarm SMS.

- CID (Contact ID protocol), support reuse of phone.

- 8 LCD programming keyboard,

- Remote control can arm/unarm host.

- Remote configuration host.

- Remote user control, event retrieve.

- Up to 5000 local logs.

- Dual power supply back up, main/sub power supply auto switch.

## Port

Example: 16-ch Network Alarm Host. Its motherboard ports are shown in Figure 1- 1.

Figure 1- 1

| No. | Name | Note |
| --- | --- | --- |
| 1 | Alarm Input | 16-ch alarm input, G is public, A1～A16 are zone inputs |
| 2 | RS485 | A1B1 to programming keyboard |
| 3 | Police | To Police no. |
| 4 | +12V | 12V output |
| 5 | Battery | 12V DC 7AH，lead-acid battery |
| 6 | Alarm Output | 4-ch alarm output |
| 7 | 2G Module | 2G module |
| 8 | Wireless Module | Wireless module |
| 9 | Telephone | To phone |
| 10 | User Line | To user line |
| 11 | LAN | Ethernet port |
| 12 | Power Supply | Power supply |

# Device Installation and Wiring

## Device Installation

### Project Installation

The product supports wall-mount and steps are listed below:

- Open device package, take out plastic expansion bolt and self-tapping screw.

- Follow Figure 2- 1 to dig five holes on wall.

- Insert palstic expansion bold, and insert four self-tapping screws around it (do not insert the one at center for now).

- Hang the device on the screw, then insert a self-tapping screw at center.

Figure 2- 1

### Motherboard Module Installation

Network Alarm Host sometimes requires manual installation for its module which includes wireless, 2G and PSTN.

Please read the following steps:

- Open cover.

- Take out bolt and fix it on motherboard.

- Take out patch adapter and fix on wireless module.

- Align wireless module with pin in the upper-left of motherboard, and fix with screw.

- Aim the other end of adapter at screw hole on chassis and fix with screw.

- Insert antenna and fasten.

- Take out adapter and fix it on 2G module.

- Align 2G module with pin in the lower-left of motherboard, and fix with screw.

- Aim the other end of adapter at screw hole on chassis and fix with screw.

- Insert antenna and fasten.

- Align PSTN module with pin in the upper-right of motherboard, and fix with screw.

Warning:

You must align the modules with pin on motherboard. If you do not align precisely, the motherboard may be damaged.

## Wiring

### Host Wiring

Example: 16-ch Network Alarm Host, device wiring is shown in Figure 2- 2.

Figure 2- 2

### Sensor Wiring

Wiring of sensor is shown in Figure 2- 3.

Figure 2- 3

### Alarm Output Wiring

Wiring of alarm output is shown in Figure 2- 4 and Figure 2- 5.

Figure 2- 4

Figure 2- 5

# SDK Client

You can login alarm host’s SDK client to view and configure parameters of alarm host

## Login

To login alarm host SDK client:

- In “AlarmDeviceDemo\Bin” folder, double click “AlarmDevice.exe” file. System enters net SDK client homepage, see Figure 3- 1.

Figure 3- 1

- Enter device IP, port no., username and password. Click Login.

Note:

- IP: device IP address, default is 192.169.1.108.

- Port no.: default is 37777.

- Username: admin

- Password: admin

- Click logout to logout.

## Device Configuration

You can configure device on zone on/off, alarm output, arm/unarm, mobile business, network, time, bypass, serial and etc.

### Network

You can setup network including device IP address, subnet mask and gateway.

- In homepage dropdown list, select Network.

- Click config. See Figure 3- 2.

Figure 3- 2

- Enter device IP address, subnet mask, and default gateway.

- Click Setup.

Note:

- IP: device IP address, default IP is :192.168.1.108.

- Default subnet mask is:255.255.255.0.

- Default gateway is:192.168.1.1.

### Time

You can set time and get time.

- In Control&Search dropdown list, select device time.

- Click Control&Search, system shows current SDK system time, see Figure 3- 3.

Figure 3- 3

- Click Get to view current device time.

- Click Setup to set device time.

### Alarm Output

You can configure corresponding channel alarm output mode.

- In homepage dropdown list, select alarm output config.

- Click Setup. See Figure 3- 4.

Figure 3- 4

- Click get to display existing configuration.

- Configure parameters. Please refer to Chart 3- 1.

| Parameter | Note |
| --- | --- |
| Channel No. | Select configured channel no. The device supports 4-ch alarm outs. |
| Channel Name | Customize channel name. |
| Output Type | Customize output alarm name. |
| Output Mode | Select alarm output mode： Auto：Auto mode. Enforced：Enforce channel to alarm. Close：Close alarm output of channel. |

Chart 3- 1

- Click Setup.

### Arm/Unarm

- In Control&Search dropdown list, select arm/unarm.

- Click Control&Search. See Figure 3- 5.

Figure 3- 5

- Set arming/unarming.

- Arm/unarm: only selections of arming or unarming.

- Scene: only supports out mode.

- Enter password.

- Click Setup.

### Bypass

When device is in arming status, a zone is still monitoring peripheral sensor and take record, however, it will not send to users. When a device changes from unarming status to arming status, original bypass zone will become non-bypass status as in arming status.

- In Control&Search  dropdown list, select bypass.

- Click Control&Search. See Figure 3- 6.

Figure 3- 6

- Set bypass.

  - Select channel and mode, enter password.

Note:

You can select the following three modes:

- Normal: channel is in normal status.

- Bypass: If zone is bypass, when it is unarming, channel mode will return to normal.

- Isolation: If zone is isolated, when it is unarming, channel mode will still be isolated.

  - Click Setup.

Note:

After you select channel, click Search, system will auto display channel mode.

### On/Off Zone

On/off zone configuration includes local alarm input channel, zone, sensor type and alarm link.

- In homepage dropdown list on the right, select on/off zone.

- Click Setup. See Figure 3- 7.

Figure 3- 7

- Click get to display existing configuration.

- Set parameters, please refer to Chart 3- 2.

| Parameter | Note |
| --- | --- |
| Channel No. | Local alarm input channel no. |
| Name | Customize channel name. |
| Bypass | Read-only. |
| Zone Type | After unarming, zone alarm upload time. Instant zone Delay zone All-day zone |
| Enter Delay | Time enter zone, when zone type is delay zone, if enter delay is 10s, then when zone alarm is triggered, user has 10S to unarm. If user successfully unarms within 10S, it will not link alarm. Otherwise, it alarms. |
| Exit Delay | Time exit zone, when zone type is delay zone, if exit delay is 10s, then when user set arming, which come into effect in 10s. |
| Sensor Type | According to sensor type, select NO or NC. |
| Sensor Method | Device supports the following sensor method： Door Passive IR Active IR Call Button Other |
| Link | When there is alarm input, you may auto link alarm output channel, please refer to step 5. |
| Root Node No. | 0 means local zone type. |
| Level 1 Cascading Address | According to root node zone no. When root node is 0, for example local zone is 16-ch, then level 1 cascading addresses are 0~15, correspond to local zone Z1~Z16. Level 2 cascading address are not used in this case. |

Chart 3- 2

- Click  next to link setup. See Figure 3- 8.

Figure 3- 8

- (Optional) When period arming is required, you must manually set arming period, you can set different periods in different weeks by checking box next to each period. Do not check box of period you do not want to enable. Period cycle unit is week.

- Set link parameters, please refer to Chart 3- 3.

| Parameter | Note |
| --- | --- |
| Audio Call Enable | Enable audio talk call function or not, check enable if you want to use it. (not available） |
| Audio Call Calling Party | Device as calling party by default (not available) |
| Audio Call Protocol | Protocol is Cellular by default. (not available) |
| Alarm Output | Enable alarm output or not, check enable if you want to use it. |
| Alarm Output Channel | Check alarm output channel no. |
| Upload to Alarm Server | Upload to alarm server or not, check enable if you want to use it. (not available) |
| Mms | Send SMS or not. |
| Buzzer | Enable buzzer or not, check enable id you want to use it. |
| Prompt | not available |
| Link Audio File Absolute Path | not available |
| Alarm bell | Enable alarm bell or not, check enable if you want to use it. |
| Access Control | not available |
| Access Control Channel | not available |
| Access Control Opration | not available |

Chart 3- 3

- Click OK. Return to On/Off Zone configuration page.

- Click Setup to set complete.

### File Upload and Download

- In Control&Search dropdown list, select upload/download.

- Click Control&Search.

- Upload or download audio file.

- Click file, select file path.

- Click upload or download.

Overtime: When upload or download time exceeds this time limit and operation is not complete, it will return error code.

### Modify Password

You can change system password.

- In Control&Search dropdown list, select modify password.

- Click Control&Search. See Figure 3- 10.

Figure 3- 10

- Enter username, old password, new password and confirm.

- Click Modify.

### Battery Search

You can search battery’s power and status.

- In Control&Search dropdown list on the right, select battery power.

- Click Control&Search. See Figure 3- 11.

Figure 3- 11

- Click Get to search.

Note:

- Power no.: power 1 represents main power (AC 220V).

- Power status: “ON” means power supply is normal. “OFF” means power supply ha leakage, and will generate corresponding alarm event.

- Battery no.: Battery 1 represents backup battery.

- Battery capacity status: it shows current battery capacity. When battery voltage is below 10V, status is 0 and generate low-voltage alarm event.

### Mobile Business

Device supports SMS service, you can send SMS to mobile phone number in setup.

- In homepage dropdown list on the right, select mobile business configuration.

See Figure 3- 12.

Figure 3- 12

- Check enable switch to enable mobile business.

- Select SMS type as SMS, enter info title and mobile phone you want to receive SMS.

- Click Setup.

### Get Alarm Channel Status

You can search status of each alarm channel.

- In Control&Search dropdown list, select channel status.

- Click Control&Search. See Figure 3- 13.

Figure 3- 13

- Select search type, and fill in quantity of channel to search. Click Get.

Note:

- Alarm input channel: corresponding alarm source, if “status” is checked, it means alarm occurs.

- Alarm output channel: corresponding alarm output channel, if the channel is checked, it means it has output. Under NO status, it is checked when relay is closed.

- Alarm bell channel: corresponding alarm bell, checked if alarm bell has output.

- Extension module alarm input: corresponding extension alarm source, when “status” is checked, it means alarm occurs.

- Extension module alarm output: corresponding alarm output channel checked if the channel has output.

### Get Active Zone(defence area) Status

You can search if each zone is active.

- In Control&Search dropdown list, select get active zone, click Control&Search. See Figure 3- 14.

Figure 3- 14

- Click get, active zone chart will show corresponding active zone channel no. and activation time. You can cancel alarm with this informatin given.

## Device Management

### Device Capacity

In homepage click device capacity, you can see Figure 3- 15, where you can view alarm host capacity in processing alarm input/output and etc.

Figure 3- 15

### Alarm Subscription

You can subscribe alarm event and cancel alarm in channel.

In homepage click alarm subscribe, see Figure 3- 16.

Figure 3- 16

- Click subscribe event, device will report current alarm and abnormal event one by one.

- On the right in the interface, select channel no. anf event type to cancel alarm, fill in password, click cancel alarm to remove alarm event.

Note:

- After you subscribe, if alarm input is triggered, before it is triggered, device will auto report its corresponding channel and time of event. After it is triggered, device will auto report Stop event of current channel at current time.

- Power failure or vandal-proof is triggered, system will report both events.

- Alarm cancellation is a re-check after alarm source is triggered and linked output. After alarm is cancelled, device will close corresponding alarm source’s link output.

### Alarm Bell Control

You can control alarm bell output.

In Control&Search dropdown list select alarm bell control, and click Control&Search.

See Figure 3- 17.

Figure 3- 17

- Click enable alarm bell output to start output.

- Click disable alarm bell output to stop output.

### Reboot Device

You can remotely reboot the device via API.

### Reset

You can reset device to default settings.

In Control&Search, click default, select reset all to restore all default settings.

Note:

You can only reset all for now.

### Log Management

You can view log information in log management.

- In Control&Search dropdown list, select log management, and click Control&Search. See

Figure 3- 18.

Figure 3- 18

- Select log type and time.

- Click search. Then you can start to view log.

### Delete Log

You can delete all logs by deleting log API port.

### File Search

You can search audio file name and path.

- In Control&Search dropdown list select file search and delete, click Control&Search. See Figure 3- 19.

Figure 3- 19

- Click get to view all audio file names and paths.

### Version

You can view client version information in version interface, see Figure 3- 20.

Figure 3- 20

### User

You can search user login condition via user information.

- In Control&Search dropdown list, select user info, and click Control&Search. See Figure 3- 21.

Figure 3- 21

- Select search type.

- Click start search.

### Remote Upgrade

You can remotely upgrade the device.

- In Control&Search dropdown list, select remote upgrade, and click Control&Search. See Figure 3- 22.

Figure 3- 22

- Click , select upgrading file.

- Click upgrade to remotely upgrade device.

Note:

Under normal condition, when upgrading file is uploaded successfully, device will auto reboot to upgrade.

If the device does not reboot automatically, please check if watch dog code is normal (Motherbozrd K3 dial code 1 to ON).

# Alarm Programming Keyboard

The alarm host can connect alarm programming keyboard to set arming/unarming and view its operation status.

## Wiring

Connection of device and alarm host is shown in Figure 5- 1. “B” and “A” ports are connected to alarm host for 485 communication. “-“ and “+” are GND and +12V port respectively.

When alarm host works normally, after wiring is set correctly, device will generate “DU” sound which means it is successfully powered up. Meanwhile, device LCD screen is on, indicator flashes which represent successful registration. Now keyboard and host can work.

Figure 5- 1

## Function

The device boots up, wait for the device registered to the alarm host, press the Menu button to enter the correct password, press the ENTER key to enter level 1 menu. Level 1 menu include: arm and unarm, zone settings, access control settings, other settings, communication settings, output settings, system status.

### Before Operation

- When keyboard powers on for the first time, prompt the user to set the address, it is recommended that you set a different address different keyboard.

- Press * key to enter the arming interface, press the other shortcut keys to enter the "zone1-zone16" interface, saved operation is still in arming.

- In "Save or Not?" interface, the following buttons are invalid shortcuts: arm, unarm, bypass, cancel bypass, cancel alarm.

- In "Same 485Addr Exit" interface, the following buttons are invalid shortcuts: arm, unarm, bypass, cancel bypass.

- In half input of the password, such as password: ***, the following buttons are invalid shortcuts: fire, police.

Common LCD screen prompt:

Set Fail：Host setup error.

Authority Fail：User right is not authorized to perform certain operations.

Function Fail：Host setup failed.

Unknown Command：Host version and keyboard version do not match.

Not Support：Host does not support current operation.

Time out,Try Again：No replay received for command sent.

Reading.：Reading host status.

Setting.：Host is responding keyboard setup operation.

If normally mount keyboard automatically turns in, and prompt“Same 485Addr Exit”, then a keyboard with same address exists.

Note:

When the keyboard with same address exists, you modify the keyboard address, otherwise the situation will require multiple operations before it is successful.

### About Keyboard Operation

- Press  PgUp key, PgDn keys to select the previous page, next page..

- After all configuration operations require that you enter the correct password before the configuration take effect.

- By 0-9 number keys, enter the zone number, access number. For example: 001.

- You can search parameter config result or host operating status in the "System Status", the search process do not require password.

## Arm-Unarm

The device supports to arm, unarm, bypass, cancel bypass, via main menu or shortcut key to enter configuration page.

Note:

When you select zone, you can select one, multiple or all zones. Press OK button to select, and if you press OK button again, the selection will be cancelled.

### Arm

When alarm host and sensor both work as normal, you arm zone via keyboard, alarm host will respond alarm in the zone. For example to arm zone1 and zone2.

- Long press * key, enter “zone1-zone16” interface.

- Select zone1, press OK button; select zone2 via PgDn key, and press Enter.

- Press Menu key, following instructions on LCD screen, press OK key to save.

- Enter correct password, and press OK.

### Unarm

Double press * key to enter zone1-zone16 interface, steps of unarm and arm are similar, please refer to Ch 5.3.1.

### ByPass

After entering bypass operation, designated zone sensors will fail from the entire sensor groups, bypassed zones will not be protected, arm, unarm operations are invalid.

Press # to enter "zone1-zone16" interface, bypass operation and arm operation are similar, specific steps refer to Ch 5.3.1.

### Cancel ByPass

Double press # button to enter zone1-zone16 interface, bypass cancellation operation and arm operation are similar, specific steps refer to Ch 5.3.1.

## Zone Settings

Device supports intime zone, 24-h zone, delay zone. Input range of zone no.:0~255; input format must be three digits, i.e. 001.

### Intime

Intime is valid only at arming status, and invalid at bypass and unarming status. Device receives alarm signal and trigger alarm. For example set zone2 to intime zone.

- Press Menu button to enter level 1 menu, select zone settings, and select Intime.

- LCD shows Input, you shall enter zone no. (i.e. 002).

- Press Enter button, and enter password.

### Fullday

Regardless of arming, bypass, fullday (24-h) zone is always in arming, which means it will trigger alarm right after it receives alarm signal.

Please refer to Intime section for operation.

### Delay

Delay zone setting includes enter delay and exit delay.

- Enter Delay: Time start from alarm is triggered, if during the time period no unarm operation is performed, it will alarm. (Delay time for 0 to 300 seconds). For convenience of staff operation. avoid alarm.

- Exit Delay: Time start from zone is armed, after a period of delay arming feature takes effect. (Delay time for 0 to 300 seconds). For convenience of staff operation, and when they leave zone, it will not alarm.

Example: Set zone 2 as delay zone, enter 30s delay, exit delay 20s.

- Press Menu button to enter level 1 menu, select Zone Setting, and select Delay.

- LCD screen shows “Input”, please enter “002030020”. “002” represents zone2, 030 represents enter delay 30s, and “020´represents exit delay 20s.

- Press OK button, and enter  password.

## Door Setting

### Mode

Access control working mode includes: anti-pinch and other types, represented by 1, 2, 3.

To set access control mode:

- Press Menu button to enter level 1 menu, select “Door Setting”, and select “Mode”.

- LCD screen shows “Input:”, please enter corresponding code of mode.

- Press OK, and enter password.

### Status Control

Access control status includes: on, off, represented by 1 and 0 respectively.

- Press Menu button to enter level 1 menu, select Door Setting, and select Status.

- LCD screen shows “Input:”, please input corresponding code.

- Press OK button, and enter password.

## Other Settings

Other settings includes: host reset, reboot, keyboard initialization, password change, system time, key sound.

### Reset

You can reset alarm host via keyboard and alarm host will reboot and restore default setup.

Press Menu button to enter level 1 menu, select Others Setting, and select Reset. Enter correct password, press OK button.

### Reboot

You can reboot alarm host via keyboard.

Press Menu button to enter level 1 menu, select Others Setting, and select Reboot. Enter correct password, press OK button.

### Initialization

This function allows you to initialize keyboard, and you can edit address.

Press Menu button to enter level 1 menu, select Others Setting, and select Init. Enter correct password, press OK button. The keyboard will be powered up again, and ask user to enter new 485 address. After user enters new address, press OK button. Keyboard will reboot and the address will be modified to 1.

### Password

You can set system password which must be six-digit.

- Press Menu button to enter level 1 menu. Select Others Setting, and select Password.

- LCD screen shows “Input:”, enter new password, and press OK button. LCD screen shows “Input Once More:”, not user enter the new password again, and press OK button. LCD screen shows “Password:”, enter the original password, and press OK button.

Tips:

If you miss-enter new password, you can press Menu button to return, and give up current operation. Then you can re-enter modify password interface to set.

### System Time

Device system time settings include: 1 indicates the time setting (hour, minute, second), 2 indicates the date setting (year, month, day).

Format of hour, minute, second, month and day are two digits, like: XX. Format of year is four digit, like: XXXX. Ranges of hour, minute, second are: 0 - 23,0 - 59,0 to 59 respectively. The maximum range of the year, month, day allowed are: 2000~2043,1 ~ 12,1 ~ 31 respectively.

- Press Menu button to enter level 1 menu, select Other Setting, and select System Time.

- LCD screen shows “Input:”, please enter code, and press OK button. Enter password.

- Select System Time again, LCD screen shows ”Input:”, now enter code, and press OK button, and enter password.

### Keysound

When device is powered up, sound of key is off by default.

Press Menu button to enter level 1 menu, select “Other Setting”, and select Keysound. Enter number 1, to enable sound; enter number 0 to disable sound.

## Communication Setting

### Net

Network config includes: IP address, subnet mask, gateway, port no., represented in 1, 2, 3, 4.

IP address, subnet mask, gateway format are all XXX#XXX#XXX#XXX# (# can be changed to *). Port no. range is 0~65535.

- Press Menu button to enter level 1 menu, select Comm Setting and select Net.

- LCD screen shows “Input:”, enter number code. Please note that first digit 1 represents current setting of IP address.

- Press OK button, and enter password.

Tips:

If to set port no. to 37777, then input 437777 and to set gateway to 255.255.0.0, input 3255#255#0#0#.

### Tel

Device supports setup up to 3 groups of telephone numbers. Max length of telephone number is 16 digits.

- Press Menu button to enter level 1 menu, select Comm Setting, and select Tel.

- LCD screen shows “Input:”, please input number code, and press OK button. Enter password.

- Continue to enter Tel, LCD screen shows “Input:”, please enter number code. Press OK  button and enter password.

### GSM

Device supports up to 3 groups of GSM number.

Steps to set GSM are similar to steps of telephone number.

### RS485 Address

Set device RS485 address, range 001~016 which is auto allocated by host.

### 2G

Number 1~4 have the following definitions:

1: Indicates enabled status. Then enter 1 means enabled, 0 means disabled.

2: the daily flow control strategy. Then enter 1 means the flow (unit: M), 0 means the time (unit: Min).

3: Indicates daily traffic usage limits. It ranges from 0 to 65,535.

4: Indicates flow alarm strategy. Then enter the number 1 indicates the upper limit does not exceed a preset alarm, numbers 0 means exceeds a preset limit is disconnected from the network.

Example: Enable 2G and set daily flow limit to 500.

- Press Menu button to enter level a menu, select Comm Setting, and select 2G.

- LCD screen shows “Input:”, please enter number(11 represents 2G function). Press OK button, and enter password.

- Continue to enter 2G interface, LCD screen shows “Input:”, enter number (20 represents control strategy is time). Press OK button, and enter password.

- Continue to enter 2G interface, LCD screen shows “Input:”, enter number (3500 represents daily limit of 500 minutes). Press OK button, and enter password.

### Wireless Code

Wireless code is code of host remote controller. Select Wireless Code , enter password to operate. Press Menu button to exit the interface and cancel operation on code.

Note:

“Setting…”: it is coding.

“OK”: Successful.

“Set fail”: Failed.

“Exited”: Remote control which is coding now exists.

“Over Range”: Exceed max possible connection range of remote control.

## Output Setting

### Alarm Bell

Press Menu button to enter level 1 menu, select Output Setting, and select Alarmbell. Enter 1, to enforce output enable; or enter 0 to disable.

### Alarm

Press Menu button to enter level 1 menu, select Output Setting, and select Alarm. First, enter zone no., and enter 1 to enable output; or enter 0 to disable output.

## System Status

### Zone

Press Menu button to enter level 1 menu, select System Status, and select Zone. Enter zone no., to search zone system status. The displayed content includes zone no. status (arm, unarm, bypass), alarm status (alm, unalm), zone type (intime, fullday, delay). For delay, front time is enter delay, back time is exit time.

### Door

Press Menu button to enter level 1 menu, select System Status, and select Door. Enter 1 to view access control group supported by current alarm host.

2 means to view access control working mode and status.

Tips:

If you want to search access control 2’s working mode, then enter 2002.

### Version

Press Menu button to enter level 1 menu, select System Status, and select Version. Press Menu button to view alarm programming keyboard and alarm host versions.

### System Time

Press Menu button to enter level 1 menu, select System Status, and select System Time. Press OK button to view current system time.

### Communication

Press Menu button to enter level 1 menu, elect System Status, and select Communication, enter 1: you can search host IP address, subnet mask, gateway, port no. (represented by 1, 2, 3, 4 respectively).

### AF Status

Press Menu button to enter level 1 menu, select System Status, and select AF status, press OK button to view alarm host status. LCD screen shows content of “XXXXXXXX” in either 0 or 1.

Note:

Number 0 means no, while number 1 means yes.

### Output

Press Menu button to enter level 1 menu, and select System Status, and select Output. Enter number 1 to search alarmbell status. Enter number 2 plus zone no. to search zone alarm status.

Tips:

Example: To search alarm bell status, input “1”. To search status of alarm output channel 16, input “2016”.

# FAQ

- Q: I cannot boot up the device properly after plug it to power supply.

- Input power is not correct.

- Switch power line contact is not good.

- Switch power supply is broken.

- Program upgrading error.

- Chassis internal wiring is reverse or loose.

- Alarm host motherboard is broken.

- ON mode dial switch 2 is at ON position, the configuration of ON mode is incorrect.

- Q: Alarm host will automatically reboot or frequently crashes minutes after startup

- Input voltage is unstable or too low.

- Program file is damaged.

- Alarm host hardware failure.

- Q: Unable to connect to the network after startup

- Network cable is not plugged in.

- IP, mask, gateway are not configured correctly.

- Abnormal network environment.

- Alarm host is not fully boot up.

- Alarm host hardware is broken.

- Q: Single channel, multi-channel, all alarm input without input event uploading

- Program does not match, re-upgrade the correct program.

- Switch zone is configured incorrectly, you may bypass both.

- Arming is not successful.

- No subscription of alarm event.

- Device disconnected.

- Alarm host hardware failure.

- Q: Single channel, multi-channel, all without alarm output

- Linkage is not configured correctly, without successfully enabled.

- Alarm outputs are configured as disabled.

- Cable is not connected.

- Alarm host hardware failure.

- Q: Device capacity, version, etc. cannot be searched

- Network disconnected.

- Harsh network environment, within the same network device network communication rate is too low.

- Setup error.

- Battery contact is poor or low voltage.

- Q：Alarm host cannot communicate with the keyboard

Check:

- Keyboard, power supply is normal.

- Keyboard end 120Ω resistor is at normal dial position, which is the ON position.

- Incorrect wiring.

- Alarm host serial port settings are incorrect.

- Mismatch of alarm keyboard and alarm host protocol.

- When connected to multiple keyboards, keyboard AB line’s furthest end needs additonal 120 ohm resistor to eliminate reflections and impedance matching, otherwise it will cause the keyboard to communicate instable

- Too far away.

- Q: Cannot login Client or WEB

- ActiveX controls are blocked.

- Dx8.1 or higher is not installed, upgrade the video driver.

- Network connection failure.

- Network setup problems.

- Username and password are incorrect.

- Client version does not match the version of alarm host.

- Q: Network connection is unstable

- Network instability.

- IP address conflict.

- MAC address conflicts.

- Q: Unable to disarm the alarm signal

- Alarm settings are incorrect.

- Manually open the alarm output.

- Input equipment failure or improperly connected.

- Individual versions of program issues, upgrade program to resolve.

- Q: Alarm does not work

- Alarm settings are incorrect.

- Alarm wiring is incorrect.

- Alarm input signal is not correct.

- Sensors are normally open(NO), normally closed (NC) type is inconsistent with the end of the line resistor connection.

- An alarm device simultaneously access two loops.

- Q: Cannot play downloaded file

- Player is not installed.

- DX8.1 or higher graphics acceleration software is not installed.

- Files in AVI format is played by MEDIA PLAYER, the computer is not installed with DivX503Bundle.exe plug-in.

- Win XP operating system to be installed with DivX503Bundle.exe and ffdshow-2004 1012 .exe.

- Q: Local menu advanced operation password or network password is forgotten

Please contact your local customer service staff or call the customer service phone at headquarters, we will guide you on how to resolve depending on model and version of the program that you provide.

Note:

- This manual is for reference only.

- All the designs and software here are subject to change without prior written notice.

- All trademarks and registered trademarks are the properties of their respective owners.

- If there is any uncertainty or controversy, please refer to the final explanation of us.

- Please visit our website for more information.